Contents

RS485_Steam_Meter	2

RS485_Electric_Meter	3

RS485_HF_Steam_Meter	4

RS485_HF_Digital_Water_Meter	5

RS485_AFT_Steam_Meter	6

RS485_Steam_Meter

Protocol Datasheet:

Request(hex): 2330310D

(Char): #01

|  | Start byte[1] | Address[2] | Stop byte[1] |
| --- | --- | --- | --- |
| Hex | 23 | 3031 | 0D |
| Char | # | 01 |  |

Reply(Char): =+026418.47@<CR>

|  | Start byte[1] | Signed[1] | Reading[9] | Unknown[1] | Stop byte[1] |
| --- | --- | --- | --- | --- | --- |
| Hex | 3D | 2B |  | 40 | 0D |
| Char | = | + | 026418.47 | @ |  |

Reading format:

Reading value = ASCII(Big Endianness)(with decimal point)

Eg. 026418.47(Char) => 26418.47t

** “.”is decimal point.

AVR program:

| Start byte | ‘=’ |
| --- | --- |
| Stop byte | ‘\r’ or ‘\n’ |
| BAUD | 9600 |

Middleware Config:

| Trim Before | 1 |
| --- | --- |
| Trim After | 1 |

RS485_Electric_Meter

Protocol Datasheet:

Request	(Char): !01201X170001G<CR><LF>

|  | Start byte [1] | Msg Len [3] | Slave Add [2] | Msg Type [1] | Msg body [0~246] | CheckSum [1] | Stop byte [2] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Hex | 21 | 303132 | 3031 | 58 |  |  | 0D0A |
| Char | ! | 012 | 01 | X | 170001 | G | <CR><LF> |

Reply(Char): !01601X0100458C1AU<CR><LF>

|  | Start byte[1] | Unknow[8] | Reading[8] | CheckSum[1] | Stop byte[1] |
| --- | --- | --- | --- | --- | --- |
| Hex | 21 |  |  |  | 0D0A |
| Char | ! | 01601X01 | 00458C1A | U | <CR><LF> |

Reading format:

Reading value = Hex

Eg. 00458C1A(Hex)  => 4557850 KWH (Dec)

AVR program:

| Start byte | ‘!’ |
| --- | --- |
| Stop byte | ‘\r’ or ‘\n’ |
| BAUD | 9600 |

Middleware Config:

| Trim Before | 8 |
| --- | --- |
| Trim After | 1 |

RS485_HF_Steam_Meter

Request(hex): CA3132 or 213132

|  | Start byte[1] | Address[2] |
| --- | --- | --- |
| Hex | 21 | 3132 |
| Char | ! | 12 |

** Initial address of Steam meter in HF is 12.

Reply(hex): :<01010000000011470000000000000000000000000000000000:=

|  | Start byte[2] | Unknown[4] | Reading[12] | Unknown[34] | Stop byte[2] |
| --- | --- | --- | --- | --- | --- |
| Char | :< | 0101 | 000000001147 | 00…00 | := |

Reading format:

Reading value = ASCII(Big Endianness) / 100

Eg. 000000001147(ASCII) => 11.47m3

AVR program:

| Address | 12 |
| --- | --- |
| Start byte | ‘<’ |
| Stop byte | ‘=’ |
| BAUD | 9600 |

Middleware Config:

| Trim Before | 4 |
| --- | --- |
| Trim After | 35 |

RS485_HF_Digital_Water_Meter

Protocol Datasheet:

Request(hex): 2A01042E

|  | Start byte[1] | Address[1] | Comment[1] | Stop byte[1] |
| --- | --- | --- | --- | --- |
| Hex | 2A | 01 | 04 | 2E |

**Comment = 4 means正向总量

Reply(hex): 01 04 06 43 00 00 00 04 41 AA

|  | Address | Comment | D0 | D1 | D2 | D3 | D4 | D5 | Checksum | Stop byte |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Hex | 01 | 04 | 06 | 43 | 00 | 00 | 00 | 04 | 41 | AA |

Reading format:

D0 ~ D4 : Reading

D5 : Unit

D4 = ( D4 >> 4) *10 + (D4 & 0x0F)

D3 = ( D3 >> 4) *10 + (D3 & 0x0F)

D2 = ( D2 >> 4) *10 + (D2 & 0x0F)

D1 = ( D1 >> 4) *10 + (D1 & 0x0F)

D0 = ( D0 >> 4) *10 + (D0 & 0x0F)

Total value = 100000000 * D4 + 1000000 * D3 + 10000 * D2 + 100 * D1 + D0;

| D5 | 4 |
| --- | --- |
| Unit | 0.001m3 |

** Middleware does not read the value of D5. It just be set in middleware config.

Reading value = Packed BCD( Little Endianness) / 1000

Eg. 0643000000(D0~D4)(Hex) => 4.306 m3

AVR program:

| Start byte | 0x01 |
| --- | --- |
| Stop byte | 0xAA |
| BAUD | 9600 |

Middleware Config:

| Trim Before | 1 |
| --- | --- |
| Trim After | 2 |
| Meter Ratio | 0.001 |

RS485_AFT_Steam_Meter

Protocol Datasheet:

Request(hex): 4001010204

|  | Start byte[1] | Address[1] | unknown[1] | Comment[1] | Checksum[1] |
| --- | --- | --- | --- | --- | --- |
| Hex | 40 | 01 | 01 | 02 | 04 |

**Comment = 0x02  means累积流量

Reply(hex): C0 01 04 27 35 43 52 F5

|  | Start byte[1] | Address[1] | Unknown[1] | Reading[4] | Checksum[1] |
| --- | --- | --- | --- | --- | --- |
| Hex | C0 | 01 | 04 | 27354352 | F5 |

Reading format:

Reading value = Packed BCD( Big Endianness) / 1000

Eg. 27354352(Hex) => 27354.352 m3 (kg)

AVR program:

| Start byte | 0xC0 |
| --- | --- |
| BAUD | 2400 |

** No Stop byte. Fixed total length = 8

Middleware Config:

| Trim Before | 2 |
| --- | --- |
| Trim After | 0 |
| Meter Ratio | 0.001 |